# 0193 Building access safety systems

Worksection abstract

This worksection Template is applicable to the design, supply, installation and maintenance of building access safety systems comprising personal equipment for working at height and rope access systems. It includes anchors and accessories for rope access and ladders for roof safety systems.

How to use this worksection

This worksection Template must be customised for each project. See A guide to NATSPEC worksections (www.natspec.com.au) for information on Template structure, word styles, and completing a worksection.

Related material located elsewhere in NATSPEC

If a listed worksection is not part of your subscription package and you wish to purchase it, contact NATSPEC.

Related material may be found in other worksections. See for example:

0341 Structural steelwork for steel framing in buildings.

0342 Light steel framing.

0381 Structural timber for timber framing in buildings.

0382 Light timber framing.

0411 Waterproofing – external and tanking for roof tanking and membrane.

0421 Roofing – combined for roof covering.

0431 Cladding – combined for lightweight external cladding.

0552 Metalwork – fabricated for stairs, ladders, guardrailing and balustrades.

Cross references

Other worksections that cross reference this worksection are:

None, but roofing/cladding worksections in a project specific worksection may cross reference this worksection.

Material not included in NATSPEC

Some projects may include items not covered by NATSPEC. For these you may need to create new text or modify this text or a suitable worksection for example guardrailing, platforms and walkway systems.

Documenting this and related work

You may document this and related work as follows:

Fall protection system: General arrangement to your office documentation policy as appropriate to brief the contractor.

Coordinate this worksection with the project roofing and or cladding worksection, as appropriate.

The Normal style text of this worksection may refer to items as being documented elsewhere in the contract documentation. Make sure they are documented.

Search acumen.architecture.com.au, the Australian Institute of Architects’ practice advisory subscription service, for notes on the following:

Safety in design.

## General

### Responsibilities

#### General

Requirement: Provide building access safety systems, as documented.

Documented is defined in 0171 General requirements as meaning contained in the contract documents.

It is the designer’s responsibility to document a general arrangement that fulfills the WHS requirements of the appropriate state or territory authority.

#### Performance

Roofing and cladding: Maintain waterproofing integrity without damage or distortion. Maintain the structural integrity of the supporting elements.

### Design

This worksection can be used to document a variety of design and construct approaches in which the designer and contractor have responsibility for different scopes of documentation.

Refer to NATSPEC TECHreport TR 03 on specifying design and construct for mechanical services which covers key principles that can be applied to other types of work more generally. Refer to NATSPEC TECHreport TR 06 for a comparison of responsibilities under different procurement systems including Design and Construct (D&C).

In arrangements where the designer is to be responsible for providing a fully documented design showing all necessary design details for construction by the contractor, this clause can be deleted.

The Australian Rope Access Association (ARAA) Industrial rope access method defines rope access operator levels and recommends that the design of roof access safety systems be undertaken by a Level 3 rope access operator in conjunction with an engineer.

AS/NZS 1891.4 clause 1.6 sets out the hierarchy of risk control as follows:

Hazard identification and risk assessment.

Elimination.

Substitution.

Isolation.

Fall protection.

Fall restraint systems: Requires minimal level of end user competency. The risk of falling from height is eliminated.

Fall arrest systems: Requires a high level of user competency. There is risk of falling from height.

#### General

Designer:

Nominate the designer e.g. Equipment supplier, Professional engineer.

#### Requirements

General: To DESIGN in 0171 General requirements.

Responsibility:

For example, responsibility of design coordination.

Performance requirements:

For example, AS/NZS 1891.2 Section 4 covers system acceptance criteria and also cross references AS/NZS 1891.2 Supp 1 for prescribed configuration systems.

Authority requirements:

For example, DA conditions, WHS requirements.

Access: Provide a system for three workers at any one time, to access the following:

Full extent of gutters.

Roof mounted plant and equipment.

Roof areas within 2.5 m of fall hazards not otherwise protected by parapets or guard rails.

External façade areas including glazing.

External lighting.

Aerials and telecommunications equipment.

### Cross references

#### General

Requirement: Conform to the following:

0171 General requirements.

0171 General requirements contains umbrella requirements for all building and services worksections.

List the worksections cross referenced by this worksection. 0171 General requirements references the 018 Common requirements subgroup of worksections. It is not necessary to repeat them here. However, you may also wish to direct the contractor to other worksections where there may be work that is closely associated with this work.

NATSPEC uses generic worksection titles, whether or not there are branded equivalents. If you use a branded worksection, change the cross reference here.

### Standards

#### General

Personal equipment for working at height: To AS/NZS 1891.1, AS/NZS 1891.2, AS/NZS 1891.3, AS/NZS 1891.4 and AS 1891.5.

AS/NZS 1891.1 covers harnesses, AS/NZS 1891.2 covers horizontal lifeline and rail systems, AS/NZS 1891.2 Supp 1 covers prescribed configurations for horizontal lifelines, AS/NZS 1891.3 covers manufacturing requirements for fall-arrest devices, AS/NZS 1891.4 covers selection, safe use and maintenance of systems and devices, and AS 1891.5 covers manufacturing requirements for lanyard assemblies and pole straps.

Rope access system: To AS/NZS 4488.1, AS/NZS ISO 22846.1 and AS/NZS ISO 22846.2.

AS/NZS 4488.1 covers the specification of rope access systems, AS/NZS ISO 22846.1 and AS/NZS ISO 22846.2 cover selection, safe use and maintenance of rope access system components and assemblies.

### Interpretation

#### Abbreviations

General: For the purposes of this worksection the following abbreviations apply:

PPE: Personal protective equipment.

Edit the Abbreviations subclause to suit the project or delete, if not required. List alphabetically.

#### Definitions

General: For the purposes of this worksection the definitions given in AS/NZS 1891.1, AS/NZS 5532 and AS/NZS ISO 22846.1 apply.

### Submissions

#### Certification

General: Submit certification of installed system.

#### Design documentation

Describe the extent of documentation required. Amend to suit the project. The documentation of the design should be signed by an individual from the company who intends to take responsibility for the design, documentation and installation of the system.

General: To 0171 General requirements and the following:

Calculations: Submit calculations by a professional engineer experienced in building access safety systems.

Certification: Submit certification by a professional engineer experienced in building access safety systems design as evidence of conformance to documented requirements.

Drawings: Submit the following drawings:

Layout of anchors and system components in plan and elevation.

Proposed methods of fixing to each substrate type in the building.

Safe work method statement (SWMS) for the designed system:

#### Marking and labelling

Requirement: Samples and schedules of proposed marking and labels for each system component.

#### Operation and maintenance manuals

General: Submit a manual describing the following:

Limitations of the system.

Operation procedures and methods.

PPE user manuals.

Care and maintenance requirements.

#### Products and materials

Manufacturers data: Submit manufacturer’s data including the following:

Product data sheets.

Installation and maintenance recommendations.

Type tests: Submit results, as follows:

Personal equipment for working at height.

Rope access systems.

Fixed ladders.

Single point anchors.

Type tests are carried out off-site. However, submission of evidence of a successful type test may be called up here for requirements specified in SELECTIONS or PRODUCTS, if there are no SELECTIONS.

#### Samples

Samples required:

Identify items that are subject to client sign-off. This may involve colour matching.

#### Subcontractors

General: Submit names and contact details of proposed suppliers and installers as recommended by the manufacturer.

Evidence of experience:

Delete if supplier/installer details are not required.

#### Tests

0171 General requirements defines different tests in INTERPRETATION, Definitions and calls for an inspection and testing plan in TESTING - GENERALLY, Inspection and testing plan.

Site tests: Submit results of proof load tests of drilled-in anchors.

Tests determining if the substrate is adequate should be performed after installation and at periodic inspections. The test is usually employed on anchors drilled into masonry materials.

#### Warranties

Requirement: Submit the warranties for each type of building access safety system, as documented.

Describe the requirements of warranties in PRODUCTS or EXECUTION.

### Inspection

#### Notice

Inspection: Give notice so that inspection may be made of the following:

Shop fabricated or assembled items ready for delivery to the site.

Commencement of shop or site welding.

All equipment attachments with concealed fixings, before they are covered.

Site erected assemblies on completion of erection, before applying finishes.

Steel surfaces prepared for, and immediately before, site applied finishes.

Installation inspector: Registered height safety inspector or engineer.

Post installation inspection

Personal equipment for working at height inspection interval: Maximum 12 months.

Rope access system inspection requirements: To AS/NZS ISO 22846.2 clause 6.7.

Rope access system inspection interval: Maximum 6 months.

Hold points, if required, should be inserted here. See Guidance to MAINTENANCE.

## Products

### General

#### Product identification

General: Marked to show the following:

Manufacturer’s identification.

Installer’s contact details.

Intended location.

Load rating and direction.

Current inspection/service date.

Batch number or serial number of the components.

Edit the list to suit the project or delete if not required. Refer to AS/NZS 1891.1 clause 4.1.3, AS/NZS 1891.2 Section 5, AS/NZS 5532 and the ARAA Code Appendices on instructions, marking and site checklists.

### Fall protection systems

#### Access safety system

System:

Fall arrest or restraint system will include a combination of some or all of the following:

Harness gear and ancillary equipment.

Horizontal lifeline and rail systems.

Overhead rail systems.

Inertia reels.

Anchorage devices.

#### Anchors

Single point anchors: To AS/NZS 5532.

AS/NZS 5532 is applicable to anchor devices for use with equipment conforming to the AS/NZS 1891  series, AS/NZS 4488.1, AS/NZS ISO 22846.1 and AS/NZS ISO 22846.2. It covers manufacturing requirements for single point anchor device used for harness-based work at height.

#### Vertical lifeline and ladder systems

Product: Vertical rail systems including cables, fixed ladders, guides and fall arrestor trolleys.

Vertical lifeline system relates to components for vertical access. Make sure the documented layout allows for the transfer of the harness lanyard from the vertical to the horizontal cable and meets WHS approval.

Fixed ladders: To AS 1657.

#### Personal protective equipment (PPE)

Harness: Supply two full body harnesses to AS/NZS 1891.1 with shock absorbing lanyards to AS 1891.5.

Storage: PPE storage holdall supplied by the manufacturer.

#### Tests

Personal equipment for working at height: Tested as follows:

Harnesses: To AS/NZS 1891.1 Section 4.

Horizontal lifeline and rail systems: To AS/NZS 1891.2.

Lanyard assemblies and pole straps: To AS 1891.5 clause 3.4.

Rope access systems:

Rope grabs and descenders: Static load test to AS/NZS 4488.1 Appendix A.

Static strength: Tests are designed to test the integrity of the system.

Back-up type rope grabs and descenders: Dynamic load and performance test to AS/NZS 4488.1 Appendix B.

Dynamic performance: Tests verifying performance prediction information provided to users and installers by the system supplier.

#### Warranties

Warranty terms:

Consult with manufacturers for warranty terms.

## Execution

### Installation

#### Standards

Personal equipment for working at height: To the AS/NZS 1891 series.

Rope access systems: to AS/NZS 4488.1.

#### Subcontractor

Installer: Registered installer, approved by the manufacturer.

#### Labels and signage

General: To AS/NZS 1891.4 clause 2.2.9.

### Testing

#### Proof load test for anchors

Drilled-in anchors: Load test drilled-in anchors used in shear and not in axial tension (direct pull-out) before use.

From the ARAA permanent anchors code for rope access, which takes the conservative approach on anchor fixing to masonry and concrete that no drilled in anchor may be loaded in axial tension (pull out).

For horizontal lifeline and rail systems refer to AS/NZS 1891.4 clause 3.1.2 (g).

For rope access systems refer to AS/NZS ISO 22846.2 clause 7.7.3 for loading requirements for anchors.

### Training

#### General

Responsibilities: Coordinate the training of owner’s facilities management personnel in conformance with 0171 General requirements.

Training records: Video record all training sessions. Catalogue and include recordings with the operation and maintenance manuals.

Additional training:

List additional training requirements of personnel using the safety system. Additional training to be done by a nationally registered training organisation.

### Completion

#### Reinstatement

Extent: Repair or replace damage to the roofing and rainwater system. If the work cannot be repaired satisfactorily, replace the whole area affected.

Touch up: If it is necessary to touch up minor damage to prepainted metal roofing, do not overspray onto undamaged surfaces.

#### Cleaning

Roofing and rainwater drainage system: Remove debris, metal swarf, solder, sealants and unused materials.

#### Warranties

Requirement: Cover materials and workmanship in the terms of the warranty in the form of interlocking warranties from the supplier and installer.

Form: Against failure of materials and execution under normal environment and use conditions.

Period: As offered by the supplier/manufacturer.

Edit the required warranty form and period as negotiated. The form(s) required should be provided as part of the contract documentation.

### Maintenance

#### General

Although this clause forms part of the requirements of AS/NZS 1891.4, it could fall outside of the scope of the project head contract. If this is the case delete the clause and consider notifying those responsible for post contract maintenance.

Preventative and mandatory system maintenance: By an Accredited Height Safety Inspector/Certifier, in conformance with AS/NZS 1891.4 Section 9 and manufacturer's maintenance/recertification recommendations.

Checklist for all inspections: To AS/NZS 1891.2 Supp 1 Table 8, and AS/NZS 1891.4 Section 9 and Appendices C and D.

The installer/competent person: To AS/NZS 1891.4 clause 1.4.2.

#### Regular scheduled periodic inspections

Standard: To AS/NZS 1891.4 Section 9.

Completion certificate:

Provide inspection, testing and certification by an Accredited Installer and/or Accredited Height Safety Inspector:

Upon completion of the installation at the date for practical completion.

Upon the expiry of the defects liability period or 12 months after completion of the installation whichever is the lesser, and valid for a further 12 months period.

Record the date of the next system inspection and period of validity and display the certificate at the access points of the work area or on the individual system components where provision is made.

For continual operation of roof safety systems, previous certification and recertification documentation should be available for periodic inspection. Where documentation is unavailable, the ARAA Codes recommend treating the system as a new installation for recertification.

#### Inspection after a fall or other event

Standard: To AS/NZS 1891.4 clause 9.5.

The full or partial system should be decommissioned until assessed by an engineer or competent person until the system is repaired or re-certified.

Refer also to AS/NZS 1891.2 Supp 1 clause 9.3.

#### On-going maintenance

Certificate: Submit the completion certificates and notify the proprietor of the requirement for continued interval testing.

Roof anchors and static lines are generally tested and certified every 6 to 12 months depending on relevant states regulations.

## Selections

Schedules are a tool to specify properties required for products or systems. If the principal permits documentation of the product or system by proprietary name, some of the properties may be unnecessary and can be deleted. Document the product or system's location here and/or on the drawings with a matching product code. Refer to NATSPEC TECHnote GEN 024 for guidance on using and editing schedules.

### Fall protection systems

#### General

Type:

Select from fall restraint systems, fall arrest systems or combination of both.

#### Harness gear and ancillary equipment

Harness type:

Accessories:

#### Horizontal lifelines and rail systems

Product:

Accessories:

#### Overhead rail systems

Product:

Accessories:

#### Inertia reels

Product:

Accessories:

#### Anchorage device

Product:

A full description may eliminate some or all of the following selections.

Roof anchorage system:

e.g. Perimeter system or Ridge system.

Roof anchor fixing:

Select from surface mounted, steel purlin mounted, steel or timber roof frame mounted or concrete substrate fixed.

Roof anchor flashing:

Proprietary item, if applicable.

#### Vertical lifeline and ladder system

Proprietary access ladder:

Vertical safety system:

Cage:

Rest platform:

Permanent ladder eaves bracket:

Anchor mounting system:

Select from:

Rung mounting suitable for round, square, triangular or L shaped rung sections.

Style/stringer mounting suitable for box, T, flat or round section ladders.

Intermediate wire guide spacing:

Generally: 4 m.

External ladders subject to wind speed greater than force 12 on the Beaufort scale: 3 m. Contact the supplier for applications beyond this range.

REFERENCED DOCUMENTS

The following documents are incorporated into this worksection by reference:

AS 1657	2018	Fixed platforms, walkways, stairways and ladders - Design, construction and installation

AS/NZS 1891		Personal equipment for work at height

AS/NZS 1891.1	2020	Manufacturing requirements for full body combination and lower body harnesses

AS/NZS 1891.2	2001	Horizontal lifeline and rail systems

AS/NZS 1891.2 Supp 1	2001	Horizontal lifeline and rail systems - Prescribed configurations for horizontal lifelines (Supplement to AS/NZS 1891.2:2001)

AS/NZS 1891.3	2020	Manufacturing requirements for fall-arrest devices

AS/NZS 1891.4	2009	Selection, use and maintenance

AS 1891.5	2020	Manufacturing requirements for lanyard assemblies and pole straps

AS/NZS 4488		Industrial rope access systems

AS/NZS 4488.1	1997	Specifications

AS/NZS 5532	2013	Manufacturing requirements for single-point anchor device used for harness-based work at height

AS/NZS ISO 22846		Personal equipment for protection against falls - Rope access systems

AS/NZS ISO 22846.1	2020	Fundamental principles for a system of work

AS/NZS ISO 22846.2	2020	Code of practice

The following documents are mentioned only in the Guidance text:

AS/NZS 1891		Industrial fall-arrest systems and devices

ARAA	2005	Industrial rope access method

NATSPEC GEN 024	2021	Using NATSPEC selections schedules

NATSPEC TR 03	2018	Specifying design and construct for mechanical services

NATSPEC TR 06	2021	Procurement: past and present