Document:			ICON Water,

Guideline 19 Response for Communal laundry

Status				For Information

For the Attention of:		Client Company Name

Project Details:			Sellick Job Number

Block XX, Section XX, Suburb ACT

Development Name

Prepared

Author:  			Carl Sommerville

Signature:			(Original signed)

Date:				13 August 2020

Reviewed

Reviewer:			Brad Williams

Signature:			(Original signed)

Date:				13th August 2020

| Revision | Date | Description of Revision | Prepared | Reviewed |
| --- | --- | --- | --- | --- |
| 01 | DD/MM/YYYY | For Information | CRS | BW |

Contents

INTRODUCTION	3

1.0	SIGNED APPLICATION FORM (signature of the owner or a person who has the consent of the owner)	4

2.0	DRAINAGE DIAGRAMS AND PLANS OF SITE	4

3.0	TYPE OF PROCESS/ACTIVITY GENERATING THE LIQUID TRADE WASTE	4

4.0	CHEMICALS TO BE USED – SUPPLY MSDS	4

5.0	QUANTITY AND RATE OF DISCHARGE	4

6.0	LIKELY SUBSTANCES IN WASTE STREAMS INTENDED FOR DISCHARGE TO SEWERAGE SYSTEM	4

7.0	DETAILS OF PROPOSED PRE-TREATMENT EQUIPMENT INCLUDING OTHER INSTRUMENTATION REQUIREMENTS	4

8.0	MAINTENANCE SCHEDULE FOR PRE-TREATMENT EQUIPMENT, INCLUDING ALL PITS, PUMPS ETC./DETAILS OF MAINTENANCE PERSONNEL	4

9.0	EXPECTED QUALITY AFTER PRE-TREATMENT –	5

9.1	Sample Data, guaranteed by equipment supplier or recommended by Consultant	5

10.0	MEASURES FOR PREVENTION OF STORMWATER INGRESS TO THE SEWERAGE SYSTEM	5

11.0	CHEMICAL HANDLING AND STORAGE FACILITIES (Where Necessary)	5

12.0	WASTE DISPOSAL MANAGEMENT (Other than sewer)	5

13.0	APPLICANTS CONTACT DETAILS	5

APPENDIX A	6

APPENDIX B	7

APPENDIX C	8

- INTRODUCTION

The ANU is proposing to build a new student accommodation building comprising of 800 individual living units (bedrooms) with a central Commercial Kitchen space as well as a two Communal Laundries, one laundry will be located within Building 1 the other laundry will be located in Building 2.

The proposed development is currently in Construction Documentation design phase, this report is being issued in support of the Non Domestic Discharge to Sewer Application, to clarify the Communal Laundry usage in accordance with ICON Water Trade Waste Guideline 19 – Medium Risk requirements.

The proposed washers will be:

Brand - DEXTER

Model - T300 (C-Series)  WC0300XA

Hot water per cycle - 9.8 litres (not applicable as cold water only is being supplied to the washing machines).

Total water per cycle - 59.8 litres

Factory Set Cycle time is - 23 minutes

SIGNED APPLICATION FORM (signature of the owner or a person who has the consent of the owner)

Refer Appendix A

DRAINAGE DIAGRAMS AND PLANS OF SITE

Refer Appendix B

TYPE OF PROCESS/ACTIVITY GENERATING THE LIQUID TRADE WASTE

Small Commercial Washing Machine discharge

CHEMICALS TO BE USED – SUPPLY MSDS

Refer Appendix C for Examples of possible detergents to be used.

QUANTITY AND RATE OF DISCHARGE

- 10 Washing Machines per laundry.

- 59.8L per cycle, standard wash cycle is 23 minutes.

- Maximum assumed cycles per hour per machine is 2.

- Total hourly discharge = (2 x 59.8L) x 10 = 1196L/hr

- Assumed total daily discharged, based on an estimated (worse case) 8hrs of operation per day = 9,568L/Day

LIKELY SUBSTANCES IN WASTE STREAMS INTENDED FOR DISCHARGE TO SEWERAGE SYSTEM

- Sodium hydroxide & other alkaline salts

- Ammonia (unlikely)

- Sodium hypochlorite (unlikely)

(No dry cleaning solvents will be used)

Note: Instructions on how to operate the washing machines correctly and efficiently are located in the common laundries with details on how to identify washing machines load sizes, amount of washing powder/liquid and or fabric softener to use. Biodegradable (Green Friendly) powders, liquid and fabric softeners are to be used.

DETAILS OF PROPOSED PRE-TREATMENT EQUIPMENT INCLUDING OTHER INSTRUMENTATION REQUIREMENTS

- Washing machines have built in lint arrestors to prevent solids from contributing to blockages in the sewer network.

MAINTENANCE SCHEDULE FOR PRE-TREATMENT EQUIPMENT, INCLUDING ALL PITS, PUMPS ETC./DETAILS OF MAINTENANCE PERSONNEL

- Washing Machine lint arrestors inspected and emptied into solid waste receptacle as specified by Manufacturer or as a maximum every 3 months by ANU/Unilodge Maintenance Personnel.

EXPECTED QUALITY AFTER PRE-TREATMENT –

Sample Data, guaranteed by equipment supplier or recommended by Consultant

Recommended expected quality of washing machine water after pre-treatment will be in the order of acceptable Ph ranges outlined in Acceptance Guideline 6: Laundry and Dry Cleaning

waste. (Based on typical MSDS’s provided and further dilution of waste water through cooling pit prior to entering the sewer network).

Ammonia will be reduced to an acceptable limit of no more than 50mg/l, (based on typical MSDS’s provided).

Free Chlorine will be limited to 5mg/l (based on typical MSDS’s provided).

The above has been based on the university students only using typical domestic grad washing powders/liquids as there will be no commercial grade washing powders/liquids being used via automatic dosing units.

Water temperature shall not exceed 38 degrees when entering the sewer network, as hot water supply to washing machines will not be provided.

MEASURES FOR PREVENTION OF STORMWATER INGRESS TO THE SEWERAGE SYSTEM

Not applicable as all drainage associated with laundries is all under cover.

CHEMICAL HANDLING AND STORAGE FACILITIES (Where Necessary)

Not applicable, as students will be providing their own washing powders/liquids

WASTE DISPOSAL MANAGEMENT (Other than sewer)

Not applicable to this project

APPLICANTS CONTACT DETAILS

ANU:

Christine Allard

02 6125 6479

Sellick Consultants:

Carl Sommerville

02 6201 0200

- APPENDIX A

Copy of signed application form for reference

- APPENDIX B

Copy if drainage plans for reference

- APPENDIX C